User Guide – Heat Optimization

Introduction

The Heat Optimization app is used for monitoring and optimizing heat consumption, temperatures, and the operation of heating systems.

The purpose is to provide the user with a quick overview of:

- Current heating system operation

- Temperatures and energy consumption

- Possible faults and alarms

- Heat economy optimization options

- Possibilities for reducing CO₂ emissions

This gives a fast overview of the system status and allows settings to be adjusted so energy consumption is reduced without compromising comfort or operational reliability.

The app can be used on mobile phones, tablets, and computers via Home Assistant.

Initial Setup

Before the system can be used correctly, the most important fields must be filled with the correct values from the Home Assistant installation.

Many fields require an entity_id.

An entity_id is the name of a sensor or device in Home Assistant.

Examples

- sensor.boiler_supply

- sensor.heatpump_power

- sensor.outdoor_temperature

- binary_sensor.heating_source_running

You can find the entity_id under:

Home Assistant → Settings → Devices & Services → Entities

Dashboard

The dashboard shows the most important information:

- Current supply temperature

- Return temperature

- Outdoor temperature

- Temperature difference (Delta T)

- Power consumption

- Operating mode

- Alarms

- Recommendations

The dashboard updates automatically.

Description of Fields

Figure 1: Overview of operating status, operation score, temperature history, and active alarms.

Temperature Sensors, Limits, and Notifications

It is possible to configure the system alarm parameters.

Heating – Supply Temperature Sensor Entity

Enter the entity_id for the sensor measuring the supply temperature.

What is supply temperature?

Supply temperature is the temperature of the water sent out into the heating system.

Example

sensor.shelly_supply_temperature

Typical Sensors

- Shelly EM Gen4

- Shelly 1PM Gen4

- Shelly Add-on

- DS18B20 temperature sensors

- SHT30 temperature and humidity sensor

Heating – Return Temperature Sensor Entity

Enter the entity_id for the sensor measuring the return temperature.

What is return temperature?

Return temperature is the temperature of the water returning from the heating system.

Example

sensor.shelly_return_temperature

Heating – Outdoor Temperature Sensor Entity

Enter the entity_id for the outdoor temperature sensor.

What is it used for?

The outdoor temperature is used for:

- Heat optimization

- Frost monitoring

- Supply temperature regulation

Example

sensor.outdoor_temperature

Power and Operation

Heating – Pump Power Sensor Entity

Enter the entity_id for the power meter connected to the heat pump or circulation pump.

What is measured?

Power consumption in watts.

Example

sensor.heatpump_power

Heating – Heat Source Status Entity

Enter the entity_id for the sensor indicating whether the heat source is active.

Possible Values

- ON/OFF

- True/False

- Active/Inactive

Example

binary_sensor.heat_source_running

Notifications

Heating – Notification Service

Select which Home Assistant service should be used for notifications.

Typical Services

- persistent_notification.create

- notify.mobile_app_phone

- notify.tablet

Example

notify.mobile_app_samsung

Heating – SMS Service

Enter an SMS service if SMS messages are required.

Example

notify.sms_gateway

If the field is left empty, SMS notifications will not be used.

Heating – SMS Recipient

Enter the recipient phone number.

Example

+4512345678

Statistics and System Type

Heating – Statistics Period

Determines how far back statistics are shown.

Options

- 1 hour

- 24 hours

- 7 days

Recommendation

24 hours is recommended for normal operation monitoring.

Heating – Heating System Type

Select which type of heating system is being used.

Options

- Oil boiler

- Straw boiler

- Heat pump

- District heating

- Other

Why is this important?

The system can use different optimization rules depending on the heating system type.

Temperature Limits

Temperature Limits

- Minimum supply temperature (°C): Lowest desired supply temperature

- Maximum supply temperature (°C): Upper limit for supply temperature

- Maximum return temperature (°C): Maximum allowed return temperature before warning/alarm

- Minimum Delta T (°C): Minimum temperature difference before low Delta T alarm

- Maximum Delta T (°C): Upper Delta T limit

- Hysteresis (°C): Buffer reducing switching between states

- Frost limit (°C): Outdoor temperature limit for frost protection

History Display

The user can:

- View current values

- View min/max values for the selected period

- Compare temperature curves over time

Heating – Minimum Supply Temperature During Operation

Lowest allowed supply temperature while the system is running.

Example

45 °C

If the value is too low, an insufficient heating alarm may occur.

Heating – Maximum Supply Temperature

Maximum allowed supply temperature.

Example

80 °C

Purpose

Protects the system against overheating.

Heating – Maximum Return Temperature

Maximum allowed return temperature.

Example

45 °C

What does a high return temperature mean?

It may indicate:

- Poor heat transfer

- Excessive pump speed

- Poor regulation

Delta T

What is Delta T?

Delta T is the difference between supply and return temperatures.

Example

- Supply = 50 °C

- Return = 40 °C

- Delta T = 10 °C

A correct Delta T provides better heating economy.

Heating – Low Delta T Limit

Minimum allowed temperature difference.

Example

8 °C

A low Delta T may be caused by:

- Excessive circulation

- Poor heat transfer

- Regulation faults

Heating – High Delta T Limit

Maximum allowed temperature difference.

Example

30 °C

A high Delta T may be caused by:

- Insufficient water circulation

- Blockages

- Pump faults

Operating Options and Fields

- Heat optimization active (toggle): Enables/disables optimization algorithm

- Frost protection active (toggle): Protects the system at low outdoor temperatures

- Heating system type: Must match the physical installation

- Default statistics period: Example: 24 hours / 7 days

How to change a value

- Press the field

- Enter a new value or select from dropdown

- Save the change

The change is normally activated immediately.

Energy Consumption

Displays energy and operational consumption.

Typical Measurements

- Consumption this hour

- Consumption over 24 hours

- Consumption over 7 days

- Pump power over time

- Estimated heat production

- SCOP (efficiency factor)

Alarm Settings

Displays active and historical alarms.

Examples of alarms

- High temperature

- Low temperature

- Communication failure

- Sensor fault

- Pump stop

- Delta T too low/high

- Frost risk

Alarm Handling

- Open the alarm

- Read the fault description

- Follow the recommended action

- Acknowledge the alarm if possible

Heating – Alarm Hysteresis

Determines how much the temperature must change before the alarm resets.

Example

2 °C

Why use hysteresis?

To avoid rapid repeated alarms.

Heating – Frost Limit

Temperature at which frost alarm is activated.

Example

3 °C

Recommendation

2–5 °C is normally appropriate.

Heating – Repeat Alarm Every Minute

Determines how often the alarm repeats.

Example

30 minutes

Functions That Can Be Activated

Heat Optimization Active

Activates the complete heat optimization system.

When enabled:

- Calculations are performed

- Alarms are monitored

- Recommendations are generated

Heating Notifications Active

Enables messages and warnings.

If disabled, no notifications are sent.

Heating SMS Active

Enables SMS alarms.

Requires:

- SMS service

- Phone number

Typical Faults

Sensor Shows Unknown or Unavailable

Possible Causes

- Incorrect entity_id

- Sensor offline

- Integration error

Solution

Check the entity_id in Home Assistant.

No Notifications Received

Check that:

- Notification service is correct

- Phone app is online

- Notifications are allowed

Incorrect Temperatures

Check:

- Sensor placement

- Calibration

- Device type

Recommended Configuration

Heat Pump

| Parameter | Recommendation |
| --- | --- |
| Minimum supply | 30–45 °C |
| Maximum supply | 55 °C |
| Maximum return | 40 °C |
| Delta T | 5–10 °C |

Central Heating

| Parameter | Recommendation |
| --- | --- |
| Minimum supply | 45 °C |
| Maximum supply | 75 °C |
| Maximum return | 40 °C |
| Delta T | 10–20 °C |

Maintenance

It is recommended regularly to:

- Check sensors

- Verify temperatures

- Review alarms

- Update Home Assistant

- Check network connections

Support

If the system does not work correctly:

- Check entity_ids

- Check sensor data in Home Assistant

- Review log files

- Restart the integration or Home Assistant

Summary

Heat Optimization provides:

- Better heating economy

- Fast fault detection

- Improved operational monitoring

- Automatic alarm handling

- Better overview of the heating system

Economy

The Economy section provides an overview of price, consumption, storage, and estimated costs.

Economy Overview

- Current power: Current power consumption (W/kW)

- Operation active: Indicates whether the system is running

- Current electricity price: Price per kWh used in calculations

- Consumption this hour / 24 hours / 7 days: Energy consumption during periods

- Cost this hour / 24 hours / 7 days: Calculated energy costs

What do you see?

You get a quick “here-and-now” overview of what the system costs to operate over short and medium-term periods.

Electricity Price and Nord Pool

- Price type: Select pricing basis (e.g. Nord Pool or fixed price)

- Nord Pool price sensor: Entity ID with spot price

- Fixed electricity price: Manual price for fixed agreements

- Additional cost per kWh: Grid/transport/subscription surcharge

- VAT factor: Typically 1.25

- Calculated electricity price: Total price used in the app

Input Format

- Price fields are entered as decimals (e.g. 2.50 DKK/kWh)

- Entity fields must contain a valid sensor ID

Measurement

- Power sensor: Sensor for current power consumption

- Operation threshold (W): Minimum power before counted as “running”

- Operating time 1 hour / 24 hours / 7 days: Accumulated runtime

- Starts in 24 hours: Number of starts (indicator of start/stop frequency)

What do you see?

Whether the system runs stably or frequently starts/stops. Many starts may increase wear.

Fuel and Prices

- Fuel type: Example: electricity, oil, pellets, straw

- Fuel price fields: Price per unit (DKK/l, DKK/kg, DKK/unit)

- Heating value: Energy content per unit (kWh/unit)

- Fuel during operation: Consumption rate during operation (unit/hour)

- Efficiency: System efficiency (0–1 or % depending on setup)

- Active fuel price: Calculated effective price per unit

What do you see?

Comparable operating costs across different fuel types.

Storage and Refilling

- Storage capacity: Maximum storage

- Current storage level: Current amount

- Normal refill amount: Typical refill quantity

- Storage percentage: Fill level in %

- Remaining hours/days: Estimate based on current consumption

- Estimated next refill: Estimated refill date

- Storage after refill: Expected level after next refill

What do you see?

When fuel is expected to run out and when refilling should be planned.

Fuel Consumption

- Fuel 1 hour / 24 hours / 7 days: Consumption during selected periods

- Fuel cost 1 hour / 24 hours / 7 days: Cost per selected period

SCOP and Heat Production

- Estimated heat production 24h: Produced heating energy during period

- SCOP 24h: Seasonal efficiency during period

Interpretation

- Higher SCOP = more heat per kWh electricity/fuel

- Falling SCOP over time may indicate need for service or adjustment

Notifications

The app can send messages in case of:

- System faults

- Temperature deviations

- High energy consumption

- Communication failures

Notification Types

- Push notification

- Email

- SMS (if enabled)

Notification Fields

- Notifications active: Master toggle for alarms

- Notification service: Service name called during alarms

- Repeat alarm every (min): Alarm repeat interval

- SMS active: Enables SMS channel

- SMS service: API/service for SMS sending

- GatewayAPI sender: Display name shown to recipient

- GatewayAPI priority: Example: low/normal/high

- SMS recipients: List of phone numbers

- Number of SMS recipients: Automatic count

SMS Recipient Format

Use international format, for example:

+4512345678

Multiple numbers can be separated by commas, semicolons, or line breaks.

User Roles

Administrator

Has access to:

- All settings

- User administration

- Advanced setup

- System configuration

Operating Personnel

Has access to:

- Monitoring

- Alarm handling

- Daily operation

- Basic settings

Guest / Viewer

Can only:

- View status

- View temperatures

- View graphs

- View economy (read-only)

No changes can be made.

Practical Use

Daily Inspection

It is recommended daily to check:

- That the system is operating normally

- That temperatures are stable

- That there are no active alarms

- That energy consumption appears normal

- That economy figures are not unusually high

Good Advice for Heat Optimization

- Avoid unnecessarily high supply temperatures

- Use night/day setback

- Maintain stable temperatures

- React quickly to alarms

- Regularly check return temperature

- Monitor SCOP and daily starts

Troubleshooting

No Data Displayed

Check:

- Internet connection

- Power to the system

- Gateway/controller

- Sensor connections

- Correct entity_ids in setup

Incorrect Temperatures

Check:

- Sensor placement

- Sensor faults

- Cable connections

- Calibration

- Units (°C, kWh, W)

The App Cannot Connect

Try:

- Restart the app

- Check network

- Restart controller/gateway

- Contact administrator

Security

- Do not share login credentials

- Use strong passwords

- Log out on shared devices

- Only authorized users should change settings

Support

In case of faults or questions contact:

- System administrator

- Installer

- Service partner

Please have the following ready:

- Fault description

- Time of fault

- Alarm codes

- Screenshots from the app

- Which fields/values were changed before the fault occurred